## Solar Worksheet
Solar Equipment (Load Side Tap Only) |  |  |  |  | Roof Information
Total Maximum Inverter Output in Amps | 1 | Amp |  |  | Select Roof Type: | Pitched Shingle
Enter Number of Panels: | 1 | Panels |  |  | Select Number of Stories: |  | Select Stories: | 1
Panel Array Area in Sq. Ft. | 1 | Square Feet |  |  | Enter Point Load Per Connection (if pitched) | 1 | Lbs. | R
Enter inverter AC Output (kW) | 1 | AC kW |  |  | Enter Roof Load PSF (if flat) | 1 | PSF | R
Required Interconnection OCP (Fuse Size) | 10 | Amp Required |  |  | Is Structural Engineering Required? | NO
Main Breaker Size (Load Side Connection Only) | 1 | Amp | T |  | Maximum Connections per Truss/Rafter | 200 |  | Connections
Bus Bar Rating (Load Side Connection Only) | 1 | Amp | T |  | Is Engineering Provided? | NO
Inverter Output Conductor Size: | 10 | Amp/ | #14 | AWG Minimum Required* | Input Building Valuation ($35.65/SF) | 1 |  | T
Address:
Notes:
*Sizing based on copper wiring. See NEC table for additional wire sizing R = Pass T = Fail BLUE TEXT = Enter Information OR Make Selection
The "Pass/Fail" on this worksheet does not address permit status. Permit Approval is separate.
Note on D12: ENTER TOTAL AMPS HERE
Note on J12: SELECT ROOF TYPE HERE
Note on D13: ENTER TOTAL PANELS HERE
Note on L13: SELECT FLOOR LEVELS HERE
Note on D14: ENTER ARRAY TOTAL SQUARE FEET HERE
Note on J14: ENTER TOTAL POINT LOADS HERE
Note on D15: ENTER AC kW HERE
Note on J15: ENTER POUNDS PER SF HERE
Note on D17: ENTER BREAKER SIZE HERE
Note on D18: ENTER BUS RATING HERE
Note on J18: Select Yes or No
Note on J19: PROVIDE PROJECT VALUATION HERE ($35.65/SF)
Note on C20: PROJECT ADDRESS HERE

## PA Data (hidden)
CO: | No | Final Inspection: |  | Yes |  |  |  | CABQ Minimum Valuation
Work Definition: |  | Pitched Shingle |  |  | / PV Solar Array | 1 | kW AC | 35.65
Occ. Class: |  | U | [5 empty] | Work Description
Const. Type: |  | VB | [5 empty] | Installation of a New Roof Mounted PV Solar Array:
Square Feet: |  | 1 | SF |  |  |  |  | Pitched Shingle
No. of Panels: |  | 1 | Panels |  |  |  |  | 1 | kW AC
Min. Valuation: |  | 1 | [5 empty] | 1 | SF
Type of Work: |  | Install New PV Solar Array | [5 empty] | 1 | Panels
Reviewed By: |  | Christian Mathias
See ProjectFlow comments in: View/Edit Changemark and Checklist Items with specific corrections and locations.
1 | Rooftop-mounted systems shall be designed to structurally support the system (R909.2). - Point loads shall not exceed 45lbs per point load (loads shall not exceed 200 lbs. on single member (14.5.2.8 F (4)(b,c) NMAC). - Provide Engineering if the total added load is greater than 5 lbs./sq. ft. for ballasted system (14.5.2.8 F (4)(a) NMAC).
2 | Provide the Engineer's signature with Date. Neither shall obscure the engineer's license number, and the date shall accompany the signature (Regulation 16.39.3.12 NMAC).
3 | Provide Roof Framing plan indicating array location and mounting points
4 | All plans shall be specific to the project at 9219 Osuna Pl., NE (R106.1.1)
5
6
7
8
9
10
11
12
13
14
15
Note on N10: Common Solar Corrections: 1. Provide Specifications for project: See the following link for required documents and plans for permitting a solar project. - http://documents.cabq.gov/planning/BuildingSafety/Roof%20Mounted%20Solar%20Checklist.pdf - Provide equipment schedule for all components of system, this shall include make, model, and listing classification (i.e. module, inverter, or micro-inverter). 2. Provide block layout/placement for ballasts with number of blocks for all supports (R909.2) - “Unirac Report” 3. The roof for solar arrays shall be designed and constructed to support the loads imposed by rooftop-mounted systems (R909.2). - Attach to rafter or provide blocking method - Provide support method for all point load connections between rafters. - Provide Roof Framing plan showing actual point load locations for proposed array (R909.2). * Identify trusses/rafters and provide approximate mounting configuration. 4. Rooftop-mounted systems shall be designed to structurally support the system (R909.2). - Point loads shall not exceed 45lbs per point load (loads shall not exceed 200 lbs. on single member (14.5.2.8 F (4)(b,c) NMAC). - Provide Engineering if the total added load is greater than 5 lbs./sq. ft. for ballasted system (14.5.2.8 F (4)(a) NMAC). 5. Provide the Engineer's signature with Date. Neither shall obscure the engineer's license number, and the date shall accompany the signature (Regulation 16.39.3.12 NMAC). - An engineer may only provide engineering services in areas in which he or she is professionally qualified (Regulation 16.39.8.9.2 NMAC) - When sealed, the Engineer accepts responsibilty for all work represented §61-23-3. M. NMSA]. 6. See the following link for required documents and plans for permitting a solar project. - http://documents.cabq.gov/planning/BuildingSafety/Roof%20Mounted%20Solar%20Checklist.pdf - Identify Roof type. - Provide NTRL certified testing for racking system or provide certified structural engineering. - Provide equipment schedule for all components of system, this shall include make, model, and listing classification( i.e. module, inverter, or micro-inverter). 7. DELETE ALL DUPLICATED FILES. 8. Duplicate file uploads may not be approved for batch stamp permitting. - Please e-mail Darlene Sandoval (dsandoval@cabq.gov) or Victoria Tena (vtena@cabq.gov) to delete all duplicated file uploads. - Re-upload new plans with identical name as original (first time upload) file to be replaced. 9. All supply side taps to be labeled as service rated. 10. Show labeling and locations of placement of labels. It must comply with Article 690 of the 2017 NEC/NMEC. 11. Provide Area for Array (R106.1.1). 12. Amps exceeded for load side tap (705.12 (B). 13. Provide "Structural Engineering" stating adequacy of existing roof for system over 10 kW AC. 14. Provide a Site Plan.

## Calculators (hidden)
[6 empty] | R | T
Solar Calculator (Load Side Tap - Amps 705.12B) | [9 empty] | Roof Loading Information
Inverter: | 1 | Amps | Inverter Amps | at 125%= | 1.25 | Output Amps= | 4.167 | Fuse |  | Total Array Load | 454.92 | Lbs.
Main Breaker: | 1 | Amps | 120% | Total Amps | 1.2 | Total Output | 2.25 | 10 |  | Number of Connections | 18 | Pts.
Bus Rating: (Use Main Brkr without Bus.) | 1 | Amps | 120% | Total Amps | 1.2 | Total Output | 2.45 | 10 |  | Point Load Per Connection | 25.28 | Lbs. |  | D
T |  | T |  |  |  | T
[10 empty] | kW to Watts |  | Micro Inverter Nominal Output Current | (Inverter output based on no. of panels)
[10 empty] | 1000 | Watts | 1.21 | 1.21 | Amps
Calculators
Add | Add | Subtract | Multiply |  | Divide
115.4 | 96.76 | 339538 | 560.1 |  | 493.4
96.1 | 497.6 | 24856 | 35.65 |  | 22 |  |  |  |  | Pass/Fail
76.7 | 57.9 | 314682 | 19967.565 |  | 22.4273 | [5 empty] | Pass
57.4 |  | Solar Panels | [8 empty] | Fail
38.1 |  |  | Panel Length Inches | 69.4 | Input Millimeters | 1046 |  |  |  | Roof | Select Roof:
|  |  | Panel Width Inches | 40.8 | Convert to inches | 25.4 |  |  |  |  | Flat Roof
|  |  | Total Square Inches | 2831.52 | Total Sq. Inches | 41.1811 |  |  |  |  | Pitched Tile
|  |  | SF Conversion | 19.6633 | # of Panels | 1 |  |  |  |  | Pitched Metal
383.7 | 652.26 | Total Array SF |  |  | 716 | [5 empty] | Pitched Shingle
Solar Valuation Calculator | [10 empty] | Pitch/Flat Combo
Square Ft. of Panels | 19.6633 | Sq. Ft. | 35.65 | 700.9978 | [5 empty] | Number of stories
1
2
YES
[9 empty] | Output Conductor Size |  | NO
[9 empty] | 20 | 12 | 15
[9 empty] | 30 | 10 | 20
[9 empty] | 50 | 8 | 25
[9 empty] | 65 | 6 | 30
[9 empty] | 85 | 4 | 35
[9 empty] | 100 | 3 | 40
[9 empty] | 115 | 2 | 45
50
Note on C3: Input Inverter Nominal AC Output Current
Note on C4: Input "Service Main Breaker" Enter BUS Rating if available.
Note on B5: Author: If no bus. Rating is supplied use the Main Breaker Amperage.
Note on C5: Input "Main Breaker" amperage if Bus. Rating is not provided.
Note on E5: Mathias, Christian A.: Rating of Bus